LED safety luminaire for ceiling mounting and for lighting escape and rescue routes acc. to  DIN EN 60598-1, DIN EN 60598-2-22 und DIN EN 1838. The round zinc die-cast surface mounted luminaire consists of two parts. The ceiling mounting housing contains the mains terminals. Technical settings e.g. adressing can be carried out voltage free at the top of the luminaire wich contains the main part of the luminaire.The connection of both parts is achieved toollessly via a latching mechanism. The design shines through its clear lines. Depending on the colour choice the luminaire can adapt to a buildings design or set contrasts where it wants to.Advantages of the zinc die-cast luminaire:- mechanically robust and corrosion resistant- powder coated surface- accurate and straight lines- no weld seam or bending edgesWith modern ERT-LED technology especially efficient because of the lense system.The radiation characteristic is rotation symmetrical circular.It ensures an equal light distribution.Application of the R Lense:-in open areas, escape route cross overs-luminaire distance up to 12m

Überwachung: 
Ausführung mit automatischem Prüfsystem gemäß DIN EN 62034 Typ S inkl. Test-Taster SelfControl:
· Testergebnisse mit Störungsanalyse (Leuchtmittel, Lade- und Batteriekreis) sowie Statusanzeigen (Betrieb, Funktionstest, Betriebsdauertest) über 3 farbige LEDs
· Automatischer Funktionstest (wöchentlich)
· Automatischer Betriebsdauertest (alle 12 Monate)
· Automatische Ladeüberwachung
· Tiefentladeschutz mit Wiedereinschaltsperre
· Leerlauf- und Kurzschlussabschaltung des Wechselrichters
Material: Zink-Druckguss
Farbe: RAL 7016
Durchmesser: 104 mm

Schutzklasse: 2
Schutzart (IP): IP 40
Stoßfestigkeitsgrad IK: IK ≥ 3
Piktogramm: Nein

Leistung Dauerbetrieb: 1,8 W W
Leistung Bereitschaftsbetrieb: 0,2 W W
Lichtstrom Notbetrieb: 240 lm lm

Eingangsspannung AC: 230 V V
Anschlussquerschnitt: 2.5 mm² mm

Batterie: NIMHHT4820Q, {{Produkt - BatteryPerformance - BatteryTechnology (P:17:110)}} Batterie

Artikelnummer: EARR023SC-AZ

Zubehör:
Artikelnummer: ILD-APA-02, IL-Aufputzadapter-02  Spritzguß, weiß  Maß D=100mm H=20mm
Artikelnummer: NIMHHT4820Q, Akkupack 4,8V/2,0Ah NimH, 300mm Ltg für IL/LEM/ LPU

Fabrikat: RP-Technik GmbH
