microControl plus
Centralised safety power supply system MC with limited power (LPS) in accordance with EN 50171 and DGUV for supplying safety and emergency exit lights 230V / 216V AC/DC. Suitable for safety lighting systems in accordance with DIN VDE 0100-718, DIN VDE 0100-560, DIN EN 50172 and DIN V VDE V 0108-100-1. 
With automatic testing device and individual luminaire monitoring with individual status display per luminaire in the control unit in conjunction with system-linked electronic ballasts including monitoring module without additional data line.
 
Nominal operating time / maximum connected load depend on the battery used 
○    1h / max. 900W
○	3h / max. 400W
○    8h / max. 160W
 
Recharge time: 12 h
 
Consisting of:
 
Microprocessor control unit with dual USB interface and integrated IO module for reporting operating statuses and remote triggering of function tests and emergency light blocking.
Charging device with microprocessor-controlled charging for standard-compliant battery charging. 
Integrated switch cabinet interior lighting.
 
For accommodating up to a maximum of 3 variable circuit assemblies type DCM, each with 2 circuits, and a maximum of one 0.5A charging assembly.
Sheet steel combination cabinet, with partially partitioned electronics and battery compartment for up to 18 OGIV batteries, max. 9 Ah
Dimensions:    H=660 mm, W=350 mm, D=230 mm
Protection class:        Electronics cabinet IP 20, protection class I
            incl. wall mounting
Cable entry:    Standard from above
Exterior finish:     Textured powder coating
Colour:        RAL 7035 light grey

Brand: RP-Technik GmbH
