MidiControl
MC central emergency power supply system without power limitation in accordance with
EN 50171 and BGV A3 for supplying 230V/216V AC/DC safety and escape sign luminaires. Suitable for emergency lighting systems in accordance with DIN VDE 0100-718, DIN VDE 0100-560, DIN EN 50172, and DIN V VDE V 0108-100.
With automatic test device and individual luminaire monitoring with individual status display for each luminaire in the control unit in conjunction with system-specific electronic ballasts including a monitoring module without an additional data line.
Rated operating time *: 1h; 3h; 8h * Please underline where applicable!
... Recharging time: 12 hours
Consists of:
- Microprocessor control unit with DB25 Centronics printer interface and integrated IO module for reporting operating states and remote triggering of function tests and emergency light blocking.
Charging device with microprocessor-controlled charging for standard-compliant battery charging.
- For accommodating up to 32 variable circuit assemblies, as well as a maximum of 2 charging assemblies of 2.5A (5A) each.
- Sheet steel combination cabinet, with partially sealed electronics and battery compartments for up to 18 OGIV batteries, up to 55Ah.
Dimensions: H = 1950 mm, W = 600 mm, D = 450 mm
Protection class: Electronics cabinet IP 21, Protection Class I
Including base height 50 mm
Cable entry: Standard from the top
Exterior finish: Textured powder coating
Color: RAL 7035 light gray
Equipped with:
- pcs. Charging modules with 2.5A each for standard charging according to the battery.
- Freely programmable final circuits with 4A nominal current / max. connected load per circuit 850 VA, two-pole fuse protection (2x T6.3A fuse protection), and information buttons on the front.
- Integrated SAM08 light switch interrogation for the joint switching of emergency and general lighting, with 8 switch inputs
Integrated CCIF module for monitoring the closed-circuit current loop for open circuits and short circuits
- Integrated IO module for reporting faults via 7 potential-free changeover contacts (230V AC/6A) and 4 control inputs 18V - 250V DC or
180V - 250V AC
Battery system equipped with:
- Stationary, maintenance-free, sealed, and extremely low-gassing
Pb battery system according to VDE 0510 DIN EN 50272-2. Service life according to EUROBAT
10 years+. Includes all necessary accessories, such as fully insulated connectors, terminal covers, and operating and handling instructions.
- OGiV - Block battery .. Ah / K10 1.8V/Z, 20°C 216V
(incl. 25% aging reserve according to EUROBAT and DIN EN 50171)
- SAM08 light switch interrogation module for the joint switching of emergency and general lighting, with 8 switch inputs 185-230 VAC; two possible switching outputs for illuminating push buttons of a time-controlled staircase lighting circuit in battery operation in guest houses/accommodations, hotels, health/care/therapy centers/facilities, and high-rise buildings where the rated operating time of the power source for safety purposes is only 3 hours according to DIN V VDE V 0108-100 or DIN VDE 0100-560; supplied loose ... SAM24 light switch interrogation module for the joint switching of emergency and general lighting, with 8 switch inputs 18-250 VDC or 185-230 VAC; supplied loose
- MC-LM bus-capable three-phase mains monitoring for installation in general lighting sub-distribution boards
- MCT15(S) remote signaling device, bus-monitored remote signaling panel
According to DIN VDE 0100-718, DIN VDE 0100-560, DIN EN 50172, and DIN V VDE V 0108-100, in an impact-resistant plastic housing for alarms and notification of system statuses via LEDs and plain text.
In addition, the system can be switched to ready mode or charging mode using a built-in key switch (S), and the continuous lighting circuits can be switched to standby mode using a push button.
Order No.: MD 1;2)/(4;6;8;10;12..32)
Manufacturer: RP-Technik GmbH Emergency Lighting Systems
Item No.: MD1(2) (4 | 6 | 8 | 10 | 12.. 32)
Unit: pcs

Brand: RP-Technik GmbH
