Escape sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838  Plastic luminaire for ceiling mounting. With trapezoidally tapered bonnet secured with screws.Suitable for continuous or stand-by operation. Planning reliability thanks to tool-free, variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Material: Polycarbonate
Color: RAL 9003
Dimensions: 152 mm x 370 mm x 195 mm

Mounting method: Deckenaufbau
Protection class: 1
Protection rating (IP): IP 65
Impact restistence rate IK: IK 6
Allowed temperature DS: -25 °C to 40 °C °C
Allowed temperature BS: -25 °C to 40 °C °C
Viewing distance: 24m m
Pictogram: Set

Power maintained mode: 4,2 W W
Power non-maintained mode: 0 W W
Luminous Flux Emergency Operation: 335 lm lm

Input voltage AC: 230 V V
Connection terminals: 1.5 mm² mm

Battery: 

Article number: PFD019

Accessories:
Article number: 2PW-EB, Double - Pendulum white 500mm  pre-wired with 4-wires
Article number: 2DW-EB
Article number: DSA, cord suspension set 1,5m
Article number: PFER, PF recessed frame for wall / ceiling

Brand: RP-Technik GmbH
