Escape sign/safety luminaire in accordance with DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.
  
Plastic luminaire for wall or ceiling mounting, with bonnet secured by screws.
Suitable for continuous or stand-by operation. Planning reliability thanks to tool-free, variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Monitoring:

With integrated monitoring module with 20-digit addressing switch, for operation on a central power supply system. Automatic test system according to DIN EN 62034 type ER, in connection with a system of type MultiControl. Functions must be complied with:

- Integrated individual luminaire monitoring

- Integrated luminaire manager function

- Individual switchability in conjunction with RP ELS - central power supply system

Material: Polycarbonate

Color: RAL 9003

Dimensions: 370 mm x 105 mm x 152 mm

Mounting method: Wandaufbau

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK 5

Allowed temperature DS: -20 °C to 40 °C °C

Allowed temperature BS: -20 °C to 40 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 5,2 W W

Power non-maintained mode: 1,1 W W

Luminous Flux Emergency Operation: 300 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery:

Article number: PFW019ML

Accessories:

Article number: BALL2, Ball protection (8W) 450x280x125mm  RAL9010, for KCW, KL, LX, VX, PFW

Brand: RP-Technik GmbH