Escape sign/safety luminaire in accordance with DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.
  
Plastic luminaire for wall or ceiling mounting, with bonnet secured by screws.
Suitable for continuous or stand-by operation. Planning reliability thanks to tool-free, variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Material: Polycarbonate

Color: RAL 9003

Dimensions: 370 mm x 105 mm x 152 mm

Mounting method: Wandaufbau

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK 5

Allowed temperature DS: -25 °C to 40 °C °C

Allowed temperature BS: -25 °C to 40 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 4,5 W W

Power non-maintained mode: 0,35 W W

Luminous Flux Emergency Operation: 150 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery: NIMHHT4820Q, {{Produkt - BatteryPerformance - BatteryTechnology (P:17:110)}} Battery

Article number: PFW013-COOL

Accessories:

Article number: BALL2, Ball protection (8W) 450x280x125mm  RAL9010, for KCW, KL, LX, VX, PFW

Brand: RP-Technik GmbH