MultiControl MCX

MC centralised safety power supply system without power limitation in accordance with

EN 50171 and BGV A3 for supplying 230V / 216V AC/DC safety and escape sign luminaires. Suitable for safety lighting systems in accordance with DIN VDE 0100-718, DIN VDE 0100-560, DIN EN 50172 and DIN V VDE V 0108-100.

With automatic testing device and individual luminaire monitoring with individual status display per luminaire in the control section in conjunction with system-bound electronic ballasts including monitoring module without additional data line.

Nominal operating time *: 1h; 3h; 8h * Please underline where applicable!

Recharging time: 12 h

Microprocessor control unit with DB25 Centronics printer interface and integrated IO module for signalling operating states and remote triggering of function tests and emergency light blocking.

Charging device with microprocessor-controlled charging and the number of charging units required for standardised charging of the battery.

For holding up to max. 60 variable circuit modules, max. 3 charging modules (2.5A each).

Load-break switch (D02) for mains and battery supply (Neozed D02), connection cross-section 16 mm² as standard.

Sheet steel combination cabinet, with partially partitioned electronics and battery compartment incl. 50 mm base, for up to 18 OGIV batteries max. 110 Ah

Dimensions: H=1850 mm, W=800 mm, D=600 mm

Protection class: Electronics cabinet IP 21, protection class I

Cable entry: Standard from above

Exterior finish: textured powder coating

Colour: RAL 7035 light grey

Brand: RP-Technik GmbH