Escape sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Robust escape sign luminaire made of stainless steel for wall mounting. With particularly easy-to-install and service-friendly hinge mechanism. As well as cover glass in front of the pictograms to protect against vandalism.

Suitable for continuous or stand-by operation. Planning reliability due to variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, bottom, top) included as standard.

Material: Stainless Steel

Color: Edelstahl

Dimensions: 56 mm x 386 mm x 240 mm

Mounting method: Wandaufbau

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -25 °C to 40 °C °C

Allowed temperature BS: -25 °C to 40 °C °C

Viewing distance: 30m m

Pictogram: Set

Power maintained mode: 4,5 W W

Power non-maintained mode: 0 W W

Luminous Flux Emergency Operation: 300 lm lm

Input voltage AC: 230 V V

Connection terminals: 1.5 mm² mm

Battery:

Article number: V2W019

Accessories:

Article number: BALL2, Ball protection (8W) 450x280x125mm  RAL9010, for KCW, KL, LX, VX, PFW

Brand: RP-Technik GmbH