Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838. 
  
Innovative synthetic LED edge luminaire for universal mounting (wall/ceiling/integrated ceiling Mount*/brackets*). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolless and variable, use of the pictograms on-site. Set of pictograms (left, right, bottom, top) is included in the scope of delivery. 
LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

Monitoring:

With integrated monitoring module for operating on a Wireless Professional central monitoring system.

- Charge monitoring indicator on the luminaire

- Manual or automatic function test (free choice of test start time in the WirelessControl software)

- Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)

- Automatic charge monitoring

- Deep discharge protection with restart inhibit

Material: Polycarbonate

Color: RAL 9003

Dimensions: 34 mm x 250 mm x 174 mm

Mounting method: Universal

Protection class: 2

Protection rating (IP): IP 54

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -10 °C to 40 °C °C

Allowed temperature BS: -10 °C to 40 °C °C

Viewing distance: 22m m

Pictogram: Set

Power maintained mode: 3,9 W W

Power non-maintained mode: 1,5 W W

Luminous Flux Emergency Operation: 190 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery: LFP3233.01, {{Produkt - BatteryPerformance - BatteryTechnology (P:17:110)}} Battery

Article number: KSC011WL

Accessories:

Article number: DSA, cord suspension set 1,5m

Article number: KME, KM recessed frame without test button (CBS)  ABS white for KM, KSU, KSC, KMB

Article number: AWKSU, Wall bracket short 60x47mm, white  convenient for KSU, KMU

Article number: 2PW-EB.1.5M, Double - Pendulum white 1500mm  pre-wired with 4-wires

Article number: 2PW-EB.2M, Double - Pendulum white 2000mm  pre-wired with 4-wires

Article number: 2PW-EB.1M, Double - Pendulum white 1000mm  pre-wired with 4-wires

Article number: 2PW-EB, Double - Pendulum white 500mm  pre-wired with 4-wires

Brand: RP-Technik GmbH