Escape sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838
  
Plastic luminaire for ceiling mounting. With trapezoidally tapered bonnet secured with screws.
Suitable for continuous or stand-by operation. Planning reliability thanks to tool-free, variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Material: Polycarbonate

Color: RAL 9003

Dimensions: 152 mm x 370 mm x 195 mm

Mounting method: Deckenaufbau

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK 6

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 4,5 W W

Power non-maintained mode: 0,35 W W

Luminous Flux Emergency Operation: 150 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery: NIMHHT4820Q, {{Produkt - BatteryPerformance - BatteryTechnology (P:17:110)}} Battery

Article number: PFD013-COOLIP54

Accessories:

Article number: 2PW-EB, Double - Pendulum white 500mm  pre-wired with 4-wires

Article number: 2DW-EB

Article number: DSA, cord suspension set 1,5m

Article number: PFER, PF recessed frame for wall / ceiling

Article number: NIMHHT4820Q, battery pack 4,8V/2,0Ah NimH, 300mm wire (LPU,LEM)

Brand: RP-Technik GmbH