Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838. 

Cube plastic luminaire with frameless bonnet and easy-to-mount bayonet catch. Due to the stable construction, the luminaire can also be suspended by chain or rope. 

Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, bottom) as standard.

Switch-mode power supply up to 5W for LED lights Set-up of various output voltages (3.3V/5V/12V/24V) possible. The NT24 power supply can be used in conjunction with a monitoring module for use in the following emergency light system types: my-, micro-, mini-, midi and multiControl. The respective output voltage is set via the switch.

Material: Polycarbonate

Color: RAL 9003

Dimensions: 300 mm x 300 mm x 179.5 mm

Mounting method: Deckenaufbau

Protection class: 2

Protection rating (IP): IP 65

Impact restistence rate IK: IK 4

Allowed temperature DS: -20 °C to 40 °C °C

Allowed temperature BS: -20 °C to 40 °C °C

Viewing distance: 30m m

Pictogram: Set

Power maintained mode: 4,6 W W

Power non-maintained mode: 0 W W

Luminous Flux Emergency Operation: 520 lm lm

Input voltage AC: 230 V V

Connection terminals: 1.5 mm² mm

Battery:

Article number: WHXD019

Accessories:

Article number: WKO, Set out of 4 x chain eyelet  for cube luminaires

Article number: DSA-Y4M, Y wire suspension 4m as a set suitable for cube  liuminaires  Two-point attachment to the ceiling with  transverse anchors, four-point attachment to  the luminaire.

Article number: DSA-Y4M-APA, 4m cable suspension incl. mounting plate

Brand: RP-Technik GmbH