Monitoring:

With integrated monitoring module, for operation on a 24V power supply system. Automatic test system in accordance with DIN EN 62034 type ER, in conjunction with a CoreCompact system. Functions must be complied with:

- Integrated individual luminaire monitoring

- Automatic addressing via configuration wizard

- Luminaires can be individually programmed and dimmed with RP's central power supply system

- Luminaire update via the system

Material: Zinc die-cast

Color: RAL 9003

Diameter: 57 mm

Mounting method: Deckenaufbau

Protection class: 3

Protection rating (IP): IP 40

Impact restistence rate IK: IK 6

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Pictogram: Nein

Power maintained mode: 1,5 W W

Power non-maintained mode: 0,4 W W

Luminous Flux Emergency Operation: 140 lm lm

Input voltage AC: 24 V V

Connection terminals: 2.5 mm² mm

Battery:

Article number: IADL529CC

Accessories:

Brand: RP-Technik GmbH