Robust zinc die-cast escape sign luminaire for wall mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838

Properties:
- Mechanically robust and corrosion-resistant
- Powder-coated surface
- Exact edges and straight lines
- No weld seams and bending edges
- Pictogram protected inside

Suitable for continuous or stand-by operation. Planning reliability due to variable use of pictograms on site. Pictograms in accordance with DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

- Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs

- Automatic function test (weekly)

- Automatic continuous function test (every 12 months)

- Automatic charge monitoring

- Deep discharge protection with restart inhibit

- Idling and short-circuit shutdown of inverter

Material: Zinc die-cast

Color: RAL 9003

Dimensions: 58 mm x 262 mm x 188 mm

Mounting method: Wandaufbau

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK 8

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 20m m

Pictogram: Set

Power maintained mode: 3,0 W W

Power non-maintained mode: 0,9 W W

Input voltage AC: 230 V V

Connection terminals: 2,5 mm² mm

Battery: LFPN3212.01-SET

Article number: FMW401SC

Accessories:

Article number: FMWA001, Surface mounting adapter for lateral cable feed  white, plastic for FM

Article number: FMDA001, ceiling bracket, single sided white  convenient for FM

Article number: FMDA002-AZ, ceiling bracket, double sided white  convenient for FM

Article number: FMFH, flexible wall mounting for FM

Article number: FMDA001-AZ, ceiling bracket, single sided black  convenient for FM

Article number: FMDA002, ceiling bracket, double sided white  convenient for FM

Article number: LFPN3212-SET-2AKKU, LFP3212.K-SET-2AKKU

Brand: RP-Technik GmbH