Escape sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838
  
Plastic luminaire for ceiling mounting. With trapezoidally tapered bonnet secured with screws.
Suitable for continuous or stand-by operation. Planning reliability thanks to tool-free, variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top, bottom) included as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

- Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs

- Automatic function test (weekly)

- Automatic continuous function test (every 12 months)

- Automatic charge monitoring

- Deep discharge protection with restart inhibit

- Idling and short-circuit shutdown of inverter

Material: Polycarbonate

Color: RAL 9003

Dimensions: 152 mm x 370 mm x 195 mm

Mounting method: Deckenaufbau

Protection class: 1

Protection rating (IP): IP 65

Impact restistence rate IK: IK 6

Allowed temperature DS: -15 °C to 40 °C °C

Allowed temperature BS: -15 °C to 40 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 5,7 W W

Power non-maintained mode: 2 W W

Luminous Flux Emergency Operation: 320 lm lm

Input voltage AC: 250 V V

Connection terminals: 2,5 mm² mm

Battery: LFPN3233.01-TT-SET

Article number: PFD411SC-TT

Accessories:

Article number: 2PW-EB, Double - Pendulum white 500mm  pre-wired with 4-wires

Article number: 2DW-EB

Article number: DSA, cord suspension set 1,5m

Article number: PFER, PF recessed frame for wall / ceiling

Article number: LFP3233.01-TT-SET-2AKKUS, LiFePO4 3,2V /  3,3Ah, low temperature

Brand: RP-Technik GmbH