Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838. 
  
Slim, elegant, convexe, synthetic luminaire tilted towards the viewer, continuously symmetrically tapered towards the bottom. For universal mounting (wall/ceiling surface mount/integrated ceiling Mount*/brackets*). For mounting convenience, the luminaire consists of only 3 parts. Toollessly mountable onto the integrated quick assembly ceiling mounting or wall mounting system. The luminaire has zero potential when dismanteled. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolfree and variable, use of the pictograms on-site. Set of pictograms (left, right, bottom, top) is included in the scope of delivery. 
LED converter with an integrated monitoring circuit for single luminaire surveillance including a 20-digit control panel with switching option.

*With additional adapter

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

- Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs

- Automatic function test (weekly)

- Automatic continuous function test (every 12 months)

- Automatic charge monitoring

- Deep discharge protection with restart inhibit

- Idling and short-circuit shutdown of inverter

Material: Polycarbonate

Color: RAL 9003

Diameter: 100 mm

Mounting method: Schienensysteme

Protection class: 2

Protection rating (IP): IP 43

Impact restistence rate IK: IK 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 24m m

Pictogram: Set

Power maintained mode: 3,3 W W

Power non-maintained mode: 1 W W

Luminous Flux Emergency Operation: 35 lm lm

Input voltage AC: 230 V V

Connection terminals: 2.5 mm² mm

Battery: LFPN3216.01

Article number: KMMU418SC-3P

Accessories:

Article number: DSA, cord suspension set 1,5m

Article number: KME-EB, KM recessed frame with test button (SB)  ABS white for KM, KSU, KSC, KMB, KMUK,  KMMU

Article number: KMBE, concrete recessed housing  for KME

Article number: AWKSU, Wall bracket short 60x47mm, white  convenient for KSU, KMU

Article number: 2PW-EB, Double - Pendulum white 500mm  pre-wired with 4-wires

Article number: BALLPLX-KMU.01, Ball protection 380x280x60mm incl. fastening  (inside dimension 300x200x50mm) Plexiglas  clear for KMU, KSU, KSC, ASMU

Brand: RP-Technik GmbH