Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22

Cube plastic luminaire with frameless bonnet and concealed mounting tray made of galvanised sheet steel. 
 
Suitable for continuous or stand-by operation. Planning reliability due to logically printed pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, top) as standard.

Monitoring:

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

- Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs

- Automatic function test (weekly)

- Automatic continuous function test (every 12 months)

- Automatic charge monitoring

- Deep discharge protection with restart inhibit

- Idling and short-circuit shutdown of inverter

Material: Metal

Color: RAL 9003

Dimensions: 237 mm x 237 mm x 237 mm

Mounting method: Wandaufbau

Protection class: 1

Protection rating (IP): IP 20

Impact restistence rate IK: IK ≥ 3

Allowed temperature DS: -5 °C to 40 °C °C

Allowed temperature BS: -5 °C to 40 °C °C

Viewing distance: 46m m

Pictogram: Set

Power maintained mode: 3,9 W W

Power non-maintained mode: 2 W W

Luminous Flux Emergency Operation: 190 lm lm

Input voltage AC: 250 V V

Connection terminals: 2,5 mm² mm

Battery: LFPN3233.01-SET

Article number: WGW418SC

Accessories:

Article number: WKO, Set out of 4 x chain eyelet  for cube luminaires

Article number: LFP3233-SET-2AKKU

Brand: RP-Technik GmbH