Escape sign luminaire in accordance with DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Plastic LED escape sign luminaire with convex moulded cover for wall mounting. Suitable for permanent or standby switching. Levelling screws are integrated to facilitate installation and compensate for uneven surfaces. Planning reliability is ensured by tool-free, variable use of the pictograms on site. The pictograms are internal and are inserted solvent-free. The pictogram set (MTL, MTR and 2x straight arrows) is included as standard.

Material: PCABS,Polycarbonate

Color: RAL 9003

Dimensions: 68 mm x 320 mm x 168 mm

Mounting method: Wandaufbau

Protection class: 2

Protection rating (IP): IP 65

Impact restistence rate IK: IK 5

Allowed temperature DS: -20 °C to 40 °C °C

Allowed temperature BS: -20 °C to 40 °C °C

Viewing distance: 30m m

Pictogram: Set

Power maintained mode: 1,6 W W

Power non-maintained mode: 0 W W

Luminous Flux Emergency Operation: 140 lm lm

Input voltage AC: 230 V V

Connection terminals: 1.5 mm² mm

Battery:

Article number: PXW019

Accessories:

Article number: PXD-PIKTOSETSONDER.01, Set consists of:  2x Rolli (R&L)  2x Arrow oblique

Brand: RP-Technik GmbH