Polycarbonate cylinder safety luminaire with explosion protection for gas and dust Ex zones. Prepared for two cable entries for feed-through wiring. By attaching a pictogram, can also be used as an emergency exit sign luminaire. Suitable for wall or ceiling mounting using mounting adapters or suspension via chain eyelet.Labelling according to 2014/34/EC (ATEX)Zone 1 / zone 21 gas and dust- Ex d IIB T6 Gb / Ex d IIB T6 Gb- Ex t IIIC T85ºC DbManufactured in accordance with-EN 60079-0:2018, EN 60079-1:2014, EN 60079-31:2014-Certified by INERIS 20ATEX0005X 

Monitoring: 
Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:
· Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
· Automatic function test (weekly)
· Automatic continuous function test (every 12 months)
· Automatic charge monitoring
· Deep discharge protection with restart inhibit
· Idling and short-circuit shutdown of inverter
Material: Aluminum die-cast,Polycarbonate
Color: Gelb
Dimensions: 750 mm x 157 mm x 197 mm

Mounting method: Universal
Protection class: 1
Protection rating (IP): IP 66
Impact restistence rate IK: IK 10
Allowed temperature DS: 0 °C to 50 °C °C
Allowed temperature BS: 0 °C to 50 °C °C
Pictogram: Nein

Power maintained mode: 45 W W
Luminous Flux Emergency Operation: 890 lm lm

Input voltage AC: 230 V V
Connection terminals: 2.5 mm² mm

Battery: 

Article number: XPMU413SC

Accessories:
Article number: X-KO001, Chain eyelets (pair) for XI / XM / XG
Article number: X-MB001, Mounting bracket (pair) wall / ceiling for XI /  XM / XG
Article number: X-KE001, Metal cable gland with strain relief for XI, XM,  XG
Article number: X4N, Pictogram set VD 14m MTO, MTU, MTL, MTR including internal holder for XI / XM / XG

Brand: RP-Technik GmbH
