Exit sign in accordance with DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Slim, elegant, convex plastic light that is inclined towards the viewer and tapers symmetrically downwards. For universal mounting (wall*/ceiling), suitable for permanent or standby operation.

The screwed cover ensures stability and a high IP protection class, while the functional technology remains unobtrusive and no screws are visible from the outside. The pictograms are inside and are inserted solvent-free for one- or two-sided labeling.

Planning security is provided by the tool-free, variable use of the pictograms on site. The pictograms in accordance with DIN ISO 7010 (2x man in the door and two arrows) are included as standard.

*with additional adapter

Monitoring:

Integrated monitoring module for operation with a DALI 2 type monitoring device

- Version with automatic test system according to DIN EN 62034; the type depends on the control unit.

- Automatic test results with fault analysis and status display (operation, function test, endurance test) centrally and at the luminaire via three LEDs.

- Manual or automatic function test configurable by group (test start time freely selectable in the DALI software).

- Configurable endurance test (every 12 months).

- Automatic charging monitoring.

- Deep discharge protection with restart lockout.

Material: PCABS,Polycarbonate

Color: RAL 9003

Dimensions: 73 mm x 339 mm x 211 mm

Mounting method: Deckenaufbau

Protection class: 2

Protection rating (IP): IP 65

Impact restistence rate IK: IK 6

Allowed temperature DS: 0 °C to 40 °C °C

Allowed temperature BS: 0 °C to 40 °C °C

Viewing distance: 30m m

Pictogram: Set

Power maintained mode: 2,9 W W

Power non-maintained mode: 0,9 W W

Luminous Flux Emergency Operation: 190 lm lm

Connection terminals: 2,5 mm² mm

Battery: LFPN3216.01

Article number: PXD413DL

Accessories:

Article number: PXD-AW, wall-parallel-bracket for the luminaire type  PXD

Article number: PXD-PIKTOSETSONDER.01, Set consists of:  2x Rolli (R&L)  2x Arrow oblique

Brand: RP-Technik GmbH