LED safety light in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.  
  
Compact emergency lighting insert with an ovally illuminating ERT LED luminaire for the ideal light distribution on emergency escape routes. With it’s clear housing material, the luminaire blends in perfectly with it’s surroundings.   
Suitable for ceiling mounting or for installation on T5/T8 illuminants. Conventional mounting supplies like clips etc. are included in the scope of delivery. Optionally available with magnetic panel. Add-on for present lights without interfering with internal wiring.

Monitoring:

With integrated monitoring module with 20-digit addressing switch, for operation on a central power supply system. Automatic test system according to DIN EN 62034 type ER, in connection with a system of type MultiControl. Functions must be complied with:

* Integrated individual luminaire monitoring
* Integrated luminaire manager function
* Individual switchability in conjunction with RP ELS - central power supply system

Material: Plastic

Color: Opal

Dimensions: 24 mm x 50 mm x 12 mm

Mounting method: Universal

Protection class: 2

Protection rating (IP): 20

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -20 to 40 °C

Allowed temperature BS: -20 to 40 °C

Pictogram: No

Power maintained mode: 2,8 W

Power non-maintained mode: 1,1 W

Luminous Flux Emergency Operation: 140 lm

Bridging time (h): CPS

Input voltage AC: 230 V

Connection terminals: 2.5 mm

Battery:

Article number: DOS029ML

Accessories:

Brand: RP-Technik