LED safety luminaire for ceiling mounting and for lighting escape and rescue routes acc. to DIN EN 60598-1, DIN EN 60598-2-22 und DIN EN 1838.

The round zinc die-cast surface mounted luminaire consists of two parts. The ceiling mounting housing contains the mains terminals. Technical settings e.g. adressing can be carried out voltage free at the top of the luminaire wich contains the main part of the luminaire.
The connection of both parts is achieved toollessly via a latching mechanism. The design shines through its clear lines. Depending on the colour choice the luminaire can adapt to a buildings design or set contrasts where it wants to.

Advantages of the zinc die-cast luminaire:
- mechanically robust and corrosion resistant
- powder coated surface
- accurate and straight lines
- no weld seam or bending edges

With modern ERT-LED technology especially efficient because of the lense system.

The radiation characteristic is contrentrally oval
Lense focused on two main directions.
Application of the F lense:
- escape routes, corridors
- luminaire distance up to 24m

Monitoring:

With integrated monitoring module for operating on a Wireless Professional central monitoring system.

* Charge monitoring indicator on the luminaire
* Manual or automatic function test (free choice of test start time in the WirelessControl software)
* Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit

Material: Zinc die-cast

Color: RAL 9003

Dimensions: x x 39 mm

Diameter: 104 mm

Mounting method: Decke

Protection class: 2

Protection rating (IP): 40

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -5 to 30 °C

Allowed temperature BS: -5 to 40 °C

Pictogram: No

Power maintained mode: 2 W

Power non-maintained mode: 0,4 W

Luminous Flux Emergency Operation: 240 lm

Bridging time (h): 3 h

Input voltage AC: 230 V

Connection terminals: 2.5 mm

Battery: NIMHHT4820Q, 4,8V/2,0Ah NiMH

Article number: EARF023WL

Accessories:

Article number: ILD-APA, IL-distance plate / cable entry

Brand: RP-Technik