Emergency sign / safety light in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
   
Slim, convex, synthetic luminaire for wall mounting. Emergency sign luminaire with pluggable, solvent-free, internal set of pictograms (left, right, bottom, top) included in the scope of delivery. Also usable as safety light without applying the pictograms, as it includes a clear-transparent cover.   
Evenly distributed illumination, due to the alligned and chromed reflector. Suitable for continuous mode or stand-by mode.

Monitoring:

With integrated monitoring module with 20-digit addressing switch, for operation on a central power supply system. Automatic test system according to DIN EN 62034 type ER, in connection with a system of type MultiControl. Functions must be complied with:

* Integrated individual luminaire monitoring
* Integrated luminaire manager function
* Individual switchability in conjunction with RP ELS - central power supply system

Material: Polycarbonate

Color: RAL 9003

Dimensions: 90 mm x 340 mm x 170 mm

Mounting method: Decke

Protection class: 1

Protection rating (IP): 64

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -20 to 40 °C

Allowed temperature BS: -20 to 40 °C

Viewing distance: 30 m

Pictogram: Set

Power maintained mode: 5,2 W

Power non-maintained mode: 1,1 W

Luminous Flux Emergency Operation: 300 lm

Bridging time (h): CPS

Input voltage AC: 230 V

Connection terminals: 2.5 mm

Battery:

Article number: KCD019ML-IP64

Accessories:

Article number: WKL, surcharge 2 x chain eyelet

Brand: RP-Technik