Emergency sign / safety light in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
   
Slim, convex, synthetic luminaire for wall mounting. Emergency sign luminaire with pluggable, solvent-free, internal set of pictograms (left, right, bottom, top) included in the scope of delivery. Also usable as safety light without applying the pictograms, as it includes a clear-transparent cover.   
Evenly distributed illumination, due to the alligned and chromed reflector. Suitable for continuous mode or stand-by mode.

Material: Polycarbonate

Color: RAL 9003

Dimensions: 90 mm x 340 mm x 170 mm

Mounting method: Decke

Protection class: 3

Protection rating (IP): 40

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -5 to 40 °C

Allowed temperature BS: -5 to 40 °C

Viewing distance: 30 m

Pictogram: Set

Power maintained mode: 3,8 W

Power non-maintained mode: 0,4 W

Luminous Flux Emergency Operation: 335 lm

Bridging time (h): CPS

Input voltage AC: 24 V

Connection terminals: 2.5 mm

Battery:

Article number: KCD519CC

Accessories:

Article number: KCAWW, KC plastic wall bracket white

Article number: DSA, cord suspension set 1,5m

Article number: 2PW-EB,

Article number: WKL, surcharge 2 x chain eyelet

Brand: RP-Technik