Emergency sign / safety light in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Slim, convex, synthetic luminaire for wall mounting. Emergency sign luminaire with pluggable, solvent-free, internal set of pictograms (left, right, bottom, top) included in the scope of delivery. Also usable as safety light without applying the pictograms, as it includes a clear-transparent cover.
Evenly distributed illumination, due to the alligned and chromed reflector. Suitable for continuous mode or stand-by mode.

Material: Polycarbonate

Color: RAL 9003

Dimensions: 60 mm x 340 mm x 170 mm

Mounting method: Universal

Protection class: 2

Protection rating (IP): 64

Impact restistence rate IK: 6

Allowed temperature DS: -20 to 40 °C

Allowed temperature BS: -20 to 40 °C

Pictogram: No

Power maintained mode: 4,6 W

Power non-maintained mode: 0 W

Luminous Flux Emergency Operation: 520 lm

Bridging time (h): CPS

Input voltage AC: 230 V

Connection terminals: 1.5 mm

Battery:

Article number: KCW029-IP64

Accessories:

Article number: BALL2, Ball protection (8W) 450x280x125mm

Article number: DWKCW, ceiling bracket KC wall

Article number: KC-IP65, KC gasket IP65 EPDM

Article number: KCER, KCW recessed frame

Article number: KCWFH, flexible wall mounting for KCW

Brand: RP-Technik