LED safety luminaire for illuminating escape and rescue routes according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.  
  
Bar-shaped plastic housing with clear trapezoidal cover for wall or ceiling mounting. Optionally, the luminaire can be installed in the ceiling with a mounting frame.  
Optimum light distribution and illumination of escape and rescue routes is achieved by using diffuser lenses and powerful LED ERT technology.

Monitoring:

With integrated monitoring module for operating on a Wireless Professional central monitoring system.

* Charge monitoring indicator on the luminaire
* Manual or automatic function test (free choice of test start time in the WirelessControl software)
* Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit

Material: Polycarbonate

Color: RAL 9003

Dimensions: 332 mm x 48 mm x 72 mm

Mounting method: Universal

Protection class: 2

Protection rating (IP): 40

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -5 to 40 °C

Allowed temperature BS: -5 to 40 °C

Pictogram: No

Power maintained mode: 7,5 W

Power non-maintained mode: 3,6 W

Luminous Flux Emergency Operation: 150 lm

Bridging time (h): 1 h

Input voltage AC: 230 V

Connection terminals: 2.5 mm

Battery: NIMH1208P, 12V/0,8Ah NiMH

Article number: KEU011WL

Accessories:

Article number: DSA, cord suspension set 1,5m

Article number: KEE-EB, KE recessed frame with test button self-contained

Article number: 2PW-EB,

Article number: 2DW-EB,

Article number: KXBE, KX concrete box 01+02

Brand: RP-Technik