Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
   
Slim synthetic luminaire for universal mounting (wall/ceiling) as well as a wall brackets via the included adapter. With additional downwards light emission. Housing can be opened without the use of tools. Suitable for continuous mode or stand-by mode. The toolless Change and variable use of the pictograms provide planning security on site. Set of pictograms (left, right, bottom, top) is included in the scope of delivery.

Material: Polycarbonate

Color: RAL 9003

Dimensions: 78 mm x 390 mm x 220 mm

Mounting method: Universal

Protection class: 2

Protection rating (IP): 43

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -25 to 40 °C

Allowed temperature BS: -25 to 40 °C

Viewing distance: 34 m

Pictogram: Set

Power maintained mode: 4,2 W

Power non-maintained mode: - W

Luminous Flux Emergency Operation: 340 lm

Bridging time (h): CPS

Input voltage AC: 24 V

Connection terminals: 1.5 mm

Battery:

Article number: KLU124

Accessories:

Article number: DSA, cord suspension set 1,5m

Article number: BALL2, Ball protection (8W) 450x280x125mm

Article number: 2PW-EB,

Article number: 2DW-EB,

Brand: RP-Technik