Emergency sign luminaire in accordance to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.

Innovative synthetic edge luminaire for universal mounting (wall/ceiling surface mount/integrated ceiling mount\*/brackets\*). Tapered housing for an appealing appearance. Suitable for continuous mode or stand-by mode. Reliable planning due to a toolless and variable, on-site use of the pictograms. Pluggable set of pictograms (left, right, down, top) is included in the scope of delivery.

Material: Polycarbonate

Color: RAL 9003

Dimensions: 48 mm x 332 mm x 242 mm

Mounting method: Universal

Protection class: 2

Protection rating (IP): 40

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -5 to 35 °C

Allowed temperature BS: -5 to 40 °C

Viewing distance: 30 m

Pictogram: Set

Power maintained mode: 3,3 W

Power non-maintained mode: 0,4 W

Luminous Flux Emergency Operation: 225 lm

Bridging time (h): 3 h

Input voltage AC: 230 V

Connection terminals: 1.5 mm

Battery: LFP3216-SET-2AKKU

Article number: KXU413SC

Accessories:

Article number: KXE-EB, KX - recessed frame SB incl. test button

Article number: AWX001, Wall bracket, white

Article number: DSA, cord suspension set 1,5m

Article number: 2PW-EB,

Article number: 2DW-EB,

Article number: KXBE, KX concrete box 01+02

Brand: RP-Technik