Emergency luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 und DIN EN 1838.   
  
Emergency luminaire in a sleek Aluminium profile, matt andonized for wall mounting with an additional light source to light the Floor below the luminaire. Housing is openable toollessly. Applicable for maintained or non-maintained operation. The toolless change and variable use of these pictograms provide planning security on site. Pluggable set of pictograms (left, right, down, up) is included in the scope of delivery.

Material: Aluminium

Color: Alu eloxiert

Dimensions: 62 mm x 258 mm x 147 mm

Mounting method: Wand

Protection class: 1

Protection rating (IP): 40

Impact restistence rate IK: 3

Allowed temperature DS: -25 to 40 °C

Allowed temperature BS: -25 to 40 °C

Viewing distance: 22 m

Pictogram: Set

Power maintained mode: 4,5 W

Power non-maintained mode: 0 W

Luminous Flux Emergency Operation: 300 lm

Bridging time (h): CPS

Input voltage AC: 230 V

Connection terminals: 1.5 mm

Battery:

Article number: LMW019

Accessories:

Article number: BALL1, Ball protection (6W) 320x220x120mm

Article number: AWM001-SI, Wall bracket, silver

Brand: RP-Technik