Escape sign luminaire according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838  
   
Metal escape sign luminaire for recessed wall mounting, with front frame secured by screws.  
   
Suitable for continuous or stand-by operation. Planning reliability due to variable use of pictograms on site. Pictograms according to DIN EN ISO 7010 and DIN ISO 3864 (left, right, bottom, top) included as standard.

Monitoring:

SC

Version with automatic test system in accordance with DIN EN 62034 type S including SelfControl test button:

* Test results with fault analysis (illuminant, charge and battery circuit) and status displays (operation, function test, continuous function test) using 3 colour LEDs
* Automatic function test (weekly)
* Automatic continuous function test (every 12 months)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit
* Idling and short-circuit shutdown of inverter

Material: Metal

Color: RAL 9003

Dimensions: 65 mm x 280 mm x 160 mm

Mounting method: Wandeinbau

Protection class: 1

Protection rating (IP): 40

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -5 to 40 °C

Allowed temperature BS: -5 to 40 °C

Viewing distance: 22 m

Pictogram: Set

Power maintained mode: 4,5 W

Power non-maintained mode: 0,35 W

Luminous Flux Emergency Operation: 150 lm

Bridging time (h): 3 h

Input voltage AC: 230 V

Connection terminals: 2.5 mm

Battery: NIMHHT4820Q, 4,8V/2,0Ah NiMH

Article number: U6E013SC

Accessories:

Article number: U6BE, U6 concreate housing

Brand: RP-Technik