Four-sided LED escape sign luminaire for ceiling mounting according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838.   
  
Cube plastic luminaire with frameless bonnet and concealed mounting tray made of galvanised sheet steel. Due to the stable construction, the luminaire can also be suspended by chain or rope.   
  
Suitable for continuous or stand-by operation. Planning reliability thanks to logically printed pictograms in accordance with DIN EN ISO 7010 and DIN ISO 3864 (left, right, top) as standard.

Monitoring:

With integrated monitoring module for operating on a Wireless Professional central monitoring system.

* Charge monitoring indicator on the luminaire
* Manual or automatic function test (free choice of test start time in the WirelessControl software)
* Manual or automatic continuous function test can be activated via the length of the luminaire’s measurement operation (free choice of test start times in the WirelessControl software)
* Automatic charge monitoring
* Deep discharge protection with restart inhibit

Material: Metal

Color: RAL 9003

Dimensions: 195 mm x 195 mm x 195 mm

Mounting method: Decke

Protection class: 1

Protection rating (IP): 20

Impact restistence rate IK: ≥ 3

Allowed temperature DS: -5 to 40 °C

Allowed temperature BS: -5 to 40 °C

Viewing distance: 36 m

Pictogram: Set

Power maintained mode: 7,5 W

Power non-maintained mode: 3,6 W

Luminous Flux Emergency Operation: 150 lm

Bridging time (h): 3 h

Input voltage AC: 230 V

Connection terminals: 2.5 mm

Battery: NIMH1208P, 12V/0,8Ah NiMH

Article number: WKD013WL

Accessories:

Article number: WKO, Set out of 4 x chain eyelet

Article number: 1PV-EB,

Brand: RP-Technik